## Bus
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu) | Area No. | AC or DC
1 | 1 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
2 | 2 | 1.045 | 0 | 0.4 | 0.424 | 0.217 | 0.127 | -0.4 | 0.5 | 1 | 1
3 | 2 | 1.01 | 0 | 0 | 0.234 | 0.942 | 0.19 | 0 | 0.4 | 1 | 1
4 | 3 | 1 | 0 | 0 | 0 | 0.478 | -0.039 | 0 | 0 | 1 | 1
5 | 3 | 1 | 0 | 0 | 0 | 0.076 | 0.016 | 0 | 0 | 1 | 1
6 | 2 | 1.07 | 0 | 0 | 0.122 | 0.112 | 0.075 | -0.06 | 0.24 | 1 | 1
7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
8 | 2 | 1.09 | 0 | 0 | 0.174 | 0 | 0 | -0.06 | 0.24 | 1 | 1
9 | 3 | 1 | 0 | 0 | 0 | 0.295 | 0.166 | 0 | 0 | 1 | 1
10 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.058 | 0 | 0 | 1 | 1
11 | 3 | 1 | 0 | 0.2 | 0 | 0.035 | 0.018 | 0 | 0 | 1 | 1
12 | 3 | 1 | 0 | 0.2 | 0 | 0.061 | 0.016 | 0 | 0 | 1 | 1
13 | 3 | 1 | 0 | 0.2 | 0 | 0.135 | 0.058 | 0 | 0 | 1 | 1
14 | 3 | 1 | 0 | 0 | 0 | 0.149 | 0.05 | 0 | 0 | 1 | 1

## Device
This sheet summarizes the devices connected to buses.
| GFL: 11 | Vdc pu | Cdc pu | wL pu | R pu | Bandwidth: vdc Hz | Bandwidth: PLL Hz | Bandwidth: idq Hz
| GFM: 20 | wLf pu | Rf pu | wCf pu | wLc pu | Rc pu | Xov pu | w droop gain Dw pu | Bandwidth: droop Hz | Bandwidth: vdq Hz | Bandwidth: idq Hz
Bus number | Device type | Device parameters
1 | 20 | 0.05 | 0.01 | 0.02 | 0.01 | 0.002 | 0 | 0.02 | 15 | 250 | 500
2 | 11 | 2.5 | 1.25 | 0.05 | 0.01 | 15 | 15 | 250
3 | 20 | 0.05 | 0.01 | 0.02 | 0.01 | 0.002 | 0 | 0.02 | 15 | 250 | 500
4 | 100
5 | 100
6 | 20 | 0.05 | 0.01 | 0.02 | 0.01 | 0.002 | 0 | 0.02 | 15 | 250 | 500
7 | 100
8 | 11 | 2.5 | 1.25 | 0.05 | 0.01 | 15 | 15 | 250
9 | 100
10 | 100
11 | 100
12 | 100
13 | 100
14 | 100

## NetworkLine_IEEE
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
UserData
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio
1 | 2 | 0.01938 | 0.05917 | 0.0528 | 0 | 1
1 | 5 | 0.05403 | 0.22304 | 0.0492 | 0 | 1
2 | 3 | 0.04699 | 0.19797 | 0.0438 | 0 | 1
2 | 4 | 0.05811 | 0.17632 | 0.034 | 0 | 1
2 | 5 | 0.05695 | 0.17388 | 0.0346 | 0 | 1
3 | 4 | 0.06701 | 0.17103 | 0.0128 | 0 | 1
4 | 5 | 0.01335 | 0.04211 | 0 | 0 | 1
4 | 7 | 0.020912 | 0.20912 | 0 | 0 | 0.978
4 | 9 | 0.055618 | 0.55618 | 0 | 0 | 0.969
5 | 6 | 0.025202 | 0.25202 | 0 | 0 | 0.932
6 | 11 | 0.09498 | 0.1989 | 0 | 0 | 1
6 | 12 | 0.12291 | 0.25581 | 0 | 0 | 1
6 | 13 | 0.06615 | 0.13027 | 0 | 0 | 1
7 | 8 | 0.017615 | 0.17615 | 0.001 | 0 | 1
7 | 9 | 0.011001 | 0.11001 | 0 | 0 | 1
9 | 10 | 0.03181 | 0.0845 | 0 | 0 | 1
9 | 14 | 0.12711 | 0.27038 | 0 | 0 | 1
10 | 11 | 0.08205 | 0.19207 | 0 | 0 | 1
12 | 13 | 0.22092 | 0.19988 | 0 | 0 | 1
13 | 14 | 0.17093 | 0.34802 | 0 | 0 | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## Basic
This sheet summarizes basic settings
Customer data:
Samping frequency (Hz) | 25000
Base frequency (Hz) | 50
Base power (VA) | 1
Base voltage (V) | 1

## Advance
This sheet summaries advanced settings.
Customer data:
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 0
Enable (plot pole map) | 1
Enable (plot admittance) | 0
Enable (print output) | 1
Enable (modal analysis) | 0

## Other Nodes
Grid-forming inverter
kvi = wv^2*Cf/4*100.
LCL filter
Grid-following inverter:
Normal PLL + LPF + PI control
LC filter but C is not 0.02 pu
PLL LPF 500Hz
SimplexPS: Version: v2021-APR-13