## PowerFlow
This sheet summarizes the parameters for power flow analysis
Notes:
Type: 1-slack bus, 2-PV bus, 3-PQ bus
The bus 1 HAVE TO be the slack bus, i.e., type-1 bus.
PGi and QGi are in generator convention. PLi and QLi are in load convention.
For active device (SG, VSI, etc), please use PGi and QGi. For load, please use PLi and QLi.
Customer data:
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu)
1 | 1 | 1.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 2 | 1.045 | 0 | 0.4 | 0.424 | 0.217 | 0.127 | -0.4 | 0.5
3 | 2 | 1.01 | 0 | 0 | 0.234 | 0.942 | 0.19 | 0 | 0.4
4 | 3 | 1 | 0 | 0 | 0 | 0.478 | -0.039 | 0 | 0
5 | 3 | 1 | 0 | 0 | 0 | 0.076 | 0.016 | 0 | 0
6 | 2 | 1.07 | 0 | 0 | 0.122 | 0.112 | 0.075 | -0.06 | 0.24
7 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 2 | 1.09 | 0 | 0 | 0.174 | 0 | 0 | -0.06 | 0.24
9 | 3 | 1 | 0 | 0 | 0 | 0.295 | 0.166 | 0 | 0
10 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.058 | 0 | 0
11 | 3 | 1 | 0 | 0.2 | 0 | 0.035 | 0.018 | 0 | 0
12 | 3 | 1 | 0 | 0.2 | 0 | 0.061 | 0.016 | 0 | 0
13 | 3 | 1 | 0 | 0.2 | 0 | 0.135 | 0.058 | 0 | 0
14 | 3 | 1 | 0 | 0 | 0 | 0.149 | 0.05 | 0 | 0

## Device
This sheet summarizes the devices connected to buses.
Notes:
For each bus, at least ONE and only ONE device can be connected.
The buses and corresponding devices CAN be listed below in arbitrary order.
The default value will be used if the corresponding customer paramter is left to blank.
The blue highlighted devices are not available currently.
For adding passive load, please use PLi and QLi in the "PowerFlow" sheet.
Device type with default values:
| Device type | Default parameters
%===============================
| 0-10: Synchronous machine | H = 3.5 pu | D = 1 pu | wL = 0.1 pu | R = 0.01 pu
0: SG (constant field flux)
1: SG (with exitation circuit)
2: SG (with prime mover control)
%===============================
| 10-19: Grid-following inverter with PLL | Vdc = 2.5 pu | Cdc = 1.25 pu | wL = 0.03 pu | R = 0.01 pu | Bandwidth vdc = 20 Hz | Bandwidth PLL = 20 Hz | Bandwidth idq = 500 Hz
10: VSI (dc-side input is Pdc)
11: VSI (fixed vdc, id_r = Pdc/vd)
12: VSI (dc-side input is idc = Pdc/vdc_r)
%===============================
| 20-29: Grid-forming inverter with frequency droop | wLf = 0.05 pu | Rf = 0.05/5 pu | wCf = 0.02 pu | wLc = 0.01 pu | Rc = 0.01/5 pu | Xov = 0 pu | w Droop Gain Dw = 5/100 pu | Bandwidth Droop = 20 Hz | Bandwidth vdq = 250 Hz | Bandwidth idq = 500 Hz
21: VSI (fixed vdc)
%===============================
| 90: Infinite bus (short circuit in small-signal) | Note: the voltage and frequency of infinite bus are setted by power flow.
%===============================
| 100: Floating bus (open circuit) | Note: the floating bus is used for the case when "no device" is connected.
%===============================
Customer data:
Bus number | Device type | Device parameters
1 | 0 | 3.5 | 5
2 | 0 | 3.5 | 5
3 | 0 | 3.5 | 5
4 | 100
5 | 100
6 | 0 | 3.5 | 5
7 | 100
8 | 0 | 3.5 | 5
9 | 100
10 | 100
11 | 100
12 | 100
13 | 100
14 | 100

## Basic
This sheet summarizes basic settings
Customer data:
Samping frequency (Hz) | 25000
Base frequency (Hz) | 50
Base power (VA) | 1
Base voltage (V) | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
Notes:
Zbranch = R+wL+1/(wC+G)
The transformer is added by turn ratio, which is connected between FromBus and Zbranch in the layout.
The branches can be listed in arbitrary order.
Mutual branch HAS TO be RL.
Self branch HAS TO be GC.
All self branch HAT TO be set, even with a very small value of wC or G.
Customer data:
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## NetworkLine_IEEE Form
This sheet summarizes the parameters for network line impedance in IEEE form.
Notes:
There is a pi-circuit between two buses, i.e., a RX impedance with BG at two terminals.
The transformer is added between FromBus and branch.
FromBus should NOT equal to ToBus in this list.
For using this sheet, please set enable from 0 to 1, then this sheet will over-write "NetworkLine"
Enable:
1
Customer data:
From bus | To bus | R (pu) | X (pu) | B/2 (pu) | G/2 (pu) | Turns Ratio
1 | 2 | 0.01938 | 0.05917 | 0.0528 | 0 | 1
1 | 5 | 0.05403 | 0.22304 | 0.0492 | 0 | 1
2 | 3 | 0.04699 | 0.19797 | 0.0438 | 0 | 1
2 | 4 | 0.05811 | 0.17632 | 0.034 | 0 | 1
2 | 5 | 0.05695 | 0.17388 | 0.0346 | 0 | 1
3 | 4 | 0.06701 | 0.17103 | 0.0128 | 0 | 1
4 | 5 | 0.01335 | 0.04211 | 0 | 0 | 1
4 | 7 | 0 | 0.20912 | 0 | 0 | 0.978
4 | 9 | 0 | 0.55618 | 0 | 0 | 0.969
5 | 6 | 0 | 0.25202 | 0 | 0 | 0.932
6 | 11 | 0.09498 | 0.1989 | 0 | 0 | 1
6 | 12 | 0.12291 | 0.25581 | 0 | 0 | 1
6 | 13 | 0.06615 | 0.13027 | 0 | 0 | 1
7 | 8 | 0 | 0.17615 | 0 | 0 | 1
7 | 9 | 0 | 0.11001 | 0 | 0 | 1
9 | 10 | 0.03181 | 0.0845 | 0 | 0 | 1
9 | 14 | 0.12711 | 0.27038 | 0 | 0 | 1
10 | 11 | 0.08205 | 0.19207 | 0 | 0 | 1
12 | 13 | 0.22092 | 0.19988 | 0 | 0 | 1
13 | 14 | 0.17093 | 0.34802 | 0 | 0 | 1

## Advanced Setting
This sheet summaries advanced settings.
Customer data:
Item | Value | Notes
Discretization method | 2 | 1-Forward Eular, 2-Hybrid Euler-Trapezoidal
Linearization times | 1 | 1-Initial step, 2-Every step
Discretization damping flag | 1 | 1-With virtual damping resistor, 2-Without virtual damping resistor
Direct feedthrough | 0 | 0-No, 1-Yes
Power flow algorithm | 2 | 1-Gauss-Seidel, 2-Newtown-Raphson
Enable (create simulink model) | 0 | 0-Disable, 1-Enable
Enable (plot pole map) | 1 | 0-Disable, 1-Enable
Enable (plot admittance) | 1 | 0-Disable, 1-Enable
Enable (print output) | 1 | 0-Disable, 1-Enable
Enable (plot swing) | 1 | 0-Disable, 1-Enable