## PowerFlow
This sheet summarizes the parameters for power flow analysis
Bus | Type | Vsp (pu) | theta (rad) | PGi (pu) | QGi (pu) | PLi (pu) | QLi (pu) | Qmin (pu) | Qmax (pu)
1 | 1 | 1 | 0 | 40 | 0 | 0 | 0 | -999 | 999
2 | 2 | 0.98 | 0 | 3.45 | 0 | 0 | 0 | -999 | 999
3 | 2 | 0.983 | 0 | 6.5 | 0 | 0 | 0 | -999 | 999
4 | 2 | 0.997 | 0 | 6.32 | 0 | 0 | 0 | -999 | 999
5 | 2 | 1.011 | 0 | 5.05 | 0 | 0 | 0 | -999 | 999
6 | 2 | 1.05 | 0 | 7 | 0 | 0 | 0 | -999 | 999
7 | 2 | 1.063 | 0 | 5.6 | 0 | 0 | 0 | -999 | 999
8 | 2 | 1.03 | 0 | 5.4 | 0 | 0 | 0 | -999 | 999
9 | 2 | 1.025 | 0 | 2 | 0 | 0 | 0 | -999 | 999
10 | 2 | 1.01 | 0 | 5 | 0 | 0 | 0 | -999 | 999
11 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999
12 | 2 | 1.0156 | 0 | 13.5 | 0 | 0 | 0 | -999 | 999
13 | 2 | 1.011 | 0 | 31.91 | 0 | 0 | 0 | -999 | 999
14 | 2 | 1 | 0 | 17.85 | 0 | 0 | 0 | -999 | 999
15 | 2 | 1 | 0 | 10 | 0 | 0 | 0 | -999 | 999
16 | 2 | 1.045 | 0 | 2.5 | 0 | 0 | 0 | -999 | 999
17 | 3 | 1 | 0 | 4 | 0 | 60 | 3 | 0 | 0
18 | 3 | 1 | 0 | 0 | 0 | 24.7 | 1.23 | 0 | 0
19 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 3 | 1 | 0 | 0 | 0 | 6.8 | 1.03 | 0 | 0
21 | 3 | 1 | 0 | 0 | 0 | 2.74 | 1.15 | 0 | 0
22 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 3 | 1 | 0 | 0 | 0 | 2.48 | 0.85 | 0 | 0
24 | 3 | 1 | 0 | 0 | 0 | 3.09 | -0.92 | 0 | 0
25 | 3 | 1 | 0 | 0 | 0 | 2.24 | 0.47 | 0 | 0
26 | 3 | 1 | 0 | 2 | 0 | 1.39 | 0.17 | 0 | 0
27 | 3 | 1 | 0 | 0 | 0 | 2.81 | 0.76 | 0 | 0
28 | 3 | 1 | 0 | 2 | 0 | 2.06 | 0.28 | 0 | 0
29 | 3 | 1 | 0 | 2 | 0 | 2.84 | 0.27 | 0 | 0
30 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
33 | 3 | 1 | 0 | 0 | 0 | 1.12 | 0 | 0 | 0
34 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
35 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | 3 | 1 | 0 | 0 | 0 | 1.02 | -0.1946 | 0 | 0
37 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
38 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
39 | 3 | 1 | 0 | 0 | 0 | 2.67 | 0.126 | 0 | 0
40 | 3 | 1 | 0 | 0 | 0 | 0.6563 | 0.2353 | 0 | 0
41 | 3 | 1 | 0 | 0 | 0 | 10 | 2.5 | 0 | 0
42 | 3 | 1 | 0 | 0 | 0 | 11.5 | 2.5 | 0 | 0
43 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
44 | 3 | 1 | 0 | 0 | 0 | 2.6755 | 0.0484 | 0 | 0
45 | 3 | 1 | 0 | 0 | 0 | 2.08 | 0.21 | 0 | 0
46 | 3 | 1 | 0 | 0 | 0 | 1.507 | 0.285 | 0 | 0
47 | 3 | 1 | 0 | 0 | 0 | 2.0312 | 0.3259 | 0 | 0
48 | 3 | 1 | 0 | 0 | 0 | 2.412 | 0.022 | 0 | 0
49 | 3 | 1 | 0 | 0 | 0 | 1.64 | 0.29 | 0 | 0
50 | 3 | 1 | 0 | 0 | 0 | 1 | -1.47 | 0 | 0
51 | 3 | 1 | 0 | 0 | 0 | 3.37 | -1.22 | 0 | 0
52 | 3 | 1 | 0 | 0 | 0 | 1.58 | 0.3 | 0 | 0
53 | 3 | 1 | 0 | 0 | 0 | 2.527 | 1.1856 | 0 | 0
54 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
55 | 3 | 1 | 0 | 0 | 0 | 3.22 | 0.02 | 0 | 0
56 | 3 | 1 | 0 | 0 | 0 | 2 | 0.736 | 0 | 0
57 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | 3 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0
59 | 3 | 1 | 0 | 1 | 0 | 2.34 | 0.84 | 0 | 0
60 | 3 | 1 | 0 | 0 | 0 | 2.088 | 0.708 | 0 | 0
61 | 3 | 1 | 0 | 0 | 0 | 1.04 | 1.25 | 0 | 0
62 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | 3 | 1 | 0 | 0 | 0 | 0.09 | 0.88 | 0 | 0
65 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 3 | 1 | 0 | 0 | 0 | 3.2 | 1.53 | 0 | 0
68 | 3 | 1 | 0 | 0 | 0 | 3.29 | 0.32 | 0 | 0

## Device
This sheet summarizes the devices connected to buses.
| 10-19: Grid-following inverter with PLL : pu | Vdc | Cdc | wL | R | Bandwidth vdc | Bandwidth PLL | Bandwidth idq
| 20-29: Grid-forming inverter with frequency droop: pu | wLf | Rf | wCf | wLc | Rc | Xov | w Droop Gain Dw | Bandwidth Droop wf | Bandwidth of vdq w_v_odq | Bandwidth of idq w_i_ldq
|  | SM | [13 empty] | EXCITER | [16 empty] | PSS
|  | X | R | x_d | x'd | x''d | T'd | T''d | xq | x'q | x''q | T'q | T''q | H | D | input filter time constant T_R | voltage regulator gain K_A | voltage regulator time constant T_A | maximum voltage regulator output V_Rmax | minimum voltage regulator output V_Rmin | exciter constant K_E | exciter time constant T_E | E_1 | S(E_1) | E_2 | S(E_2) | stabilizer gain K_F | stabilizer time constant T_F | K_P | K_I | K_D | T_D | KPSS | TW | T11 | T12 | T21 | T22 | T31 | T32 | VSSmax | VSSmin
Bus number | Device type | Device parameters
1 | 38 | 0.00205 | 0.0041 | 0.0178 | 0.00355 | 0.00275 | 7.8 | 0.05 | 0.0167 | 0.00475 | 0.00275 | 1.5 | 0.035 | 450 | 0
2 | 39 | 0.035 | 0.07 | 0.295 | 0.0697 | 0.05 | 6.56 | 0.05 | 0.282 | 0.093333 | 0.05 | 1.5 | 0.035 | 30.2 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
3 | 39 | 0.0304 | 0.0608 | 0.2495 | 0.0531 | 0.045 | 5.7 | 0.05 | 0.237 | 0.071429 | 0.045 | 1.5 | 0.035 | 35.8 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
4 | 39 | 0.0295 | 0.059 | 0.262 | 0.0436 | 0.035 | 5.69 | 0.05 | 0.258 | 0.058571 | 0.035 | 1.5 | 0.035 | 28.6 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
5 | 39 | 0.027 | 0.054 | 0.33 | 0.066 | 0.05 | 5.4 | 0.05 | 0.31 | 0.088333 | 0.05 | 0.44 | 0.035 | 26 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
6 | 39 | 0.0224 | 0.0448 | 0.254 | 0.05 | 0.04 | 7.3 | 0.05 | 0.241 | 0.0675 | 0.04 | 0.4 | 0.035 | 34.8 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
7 | 39 | 0.0322 | 0.0644 | 0.295 | 0.049 | 0.04 | 5.66 | 0.05 | 0.292 | 0.066667 | 0.04 | 1.5 | 0.035 | 26.4 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
8 | 39 | 0.028 | 0.056 | 0.29 | 0.057 | 0.045 | 6.7 | 0.05 | 0.28 | 0.076667 | 0.045 | 0.41 | 0.035 | 24.3 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
9 | 39 | 0.0298 | 0.0596 | 0.2106 | 0.057 | 0.045 | 4.79 | 0.05 | 0.205 | 0.076667 | 0.045 | 1.96 | 0.035 | 34.5 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
10 | 39 | 0.0199 | 0.0398 | 0.169 | 0.0457 | 0.04 | 9.37 | 0.05 | 0.115 | 0.061539 | 0.04 | 1.5 | 0.035 | 31 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
11 | 39 | 0.0103 | 0.0206 | 0.128 | 0.018 | 0.012 | 4.1 | 0.05 | 0.123 | 0.024118 | 0.012 | 1.5 | 0.035 | 28.2 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
12 | 39 | 0.022 | 0.044 | 0.101 | 0.031 | 0.025 | 7.4 | 0.05 | 0.095 | 0.042 | 0.025 | 1.5 | 0.035 | 92.3 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
13 | 38 | 0.0015 | 0.003 | 0.0148 | 0.00275 | 0.002 | 5.9 | 0.05 | 0.0143 | 0.0037 | 0.002 | 1.5 | 0.035 | 496 | 0
14 | 38 | 0.0017 | 0.0034 | 0.018 | 0.00285 | 0.0023 | 4.1 | 0.05 | 0.0173 | 0.0037931 | 0.0023 | 1.5 | 0.035 | 300 | 0
15 | 29 | 0.2 | 0.02 | 0.08 | 0.03 | 9.55e-06 | 0 | 0.0075 | 20 | 100 | 250
16 | 39 | 0.0125 | 0.025 | 0.1 | 0.031 | 0.025 | 10.2 | 0.05 | 0.069 | 0.041667 | 0.025 | 1.5 | 0.035 | 42 | 0 | 0.01 | 1 | 0.02 | 10 | -10 | 1 | 0.785 | 3.9267 | 0.07 | 5.2356 | 0.91 | 0.03 | 1 | 200 | 50 | 50 | 0.01 | 20 | 15 | 0.15 | 0.04 | 0.15 | 0.04 | 0.15 | 0.04 | 0.2 | -0.05
17 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
18 | 100
19 | 100
20 | 100
21 | 100
22 | 100
23 | 100
24 | 100
25 | 100
26 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
27 | 100
28 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 300
29 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 220
30 | 100
31 | 100
32 | 100
33 | 100
34 | 100
35 | 100
36 | 100
37 | 100
38 | 100
39 | 100
40 | 100
41 | 100
42 | 100
43 | 100
44 | 100
45 | 100
46 | 100
47 | 100
48 | 100
49 | 100
50 | 100
51 | 100
52 | 100
53 | 100
54 | 100
55 | 100
56 | 100
57 | 100
58 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
59 | 10 | 2.5 | 7.5 | 0.005 | 0.0016667 | 20 | 20 | 500
60 | 100
61 | 100
62 | 100
63 | 100
64 | 100
65 | 100
66 | 100
67 | 100
68 | 100
Note on B7: Zhu, Yue: Type 30: 8th order synchronous machine Type 31: 8th order synchronous machine + DC4B Exciter Type 32: 8th order synchronous machine + DC4B Exciter + 3-stage PSS Type 33: 8th order synchronous machine + TGOV1 Type 34: 8th order synchronous machine + DC4B Exciter + TGOV1 Type 35: 8th order synchronous machine + DC4B Exciter + 3-stage PSS + TGOV1 Type 38: 8th order synchronous machine + TGOV1 (Fast Stabilized mode) Type 39: 8th order synchronous machine + DC4B Exciter + 3-stage PSS + TGOV1 (Fast Stabilized mode) Type 10: Grid following inverter (go to userMain.xlsx for more instructions) Type 21: Grid forming inverter (go to userMain.xlsx for more instructions)
Note on A8: Yue Zhu: Bus 1 and Bus 16 are swapt here because in the Toolbox, bus 1 has to be the swing bus. In the results of the paper, they are swapt back.
Note on AB18: Zhu, Yue: The parameters of A11 are kept the same as the original model, but seems to be quite different compared with other nearby machine. And it is reported that A11 is considered as an unstable machine in this 68 bus system.
Note on C20: Yue Zhu: The power rating of M1 (original M16) and M13 are 2 times of others, therefore the parameters should be changed: X becomes 1/2 of the orignal, D and H becomes 2 times.
Note on I22: Yue Zhu: Deliberately detuned high.
Note on I36: Yue Zhu: deliberately detuned low.

## Basic
This sheet summarizes basic settings
Samping frequency (Hz) | 30000
Base frequency (Hz) | 60
Base power (VA) | 1
Base voltage (V) | 1

## NetworkLine
This sheet summarizes the parameters for network line impedance.
From bus | To bus | R (pu) | wL (pu) | wC (pu) | G (pu) | Turns ratio (pu)

## NetworkLine_IEEE Form
This sheet summarizes the parameters for network line impedance in IEEE form.
Enable:
1
User data:
From bus | To bus | R (pu) | X (pu) | B (pu) | G (pu) | Turns Ratio (pu)
16 | 54 | 1e-07 | 0.0181 | 0 | 0 | 1.025
2 | 58 | 1e-07 | 0.025 | 0 | 0 | 1.07
3 | 62 | 1e-07 | 0.02 | 0 | 0 | 1.07
4 | 19 | 0.0007 | 0.0142 | 0 | 0 | 1.07
5 | 20 | 0.0009 | 0.018 | 0 | 0 | 1.009
6 | 22 | 1e-07 | 0.0143 | 0 | 0 | 1.025
7 | 23 | 0.0005 | 0.0272 | 0 | 0 | 1
8 | 25 | 0.0006 | 0.0232 | 0 | 0 | 1.025
9 | 29 | 0.0008 | 0.0156 | 0 | 0 | 1.025
10 | 31 | 1e-07 | 0.026 | 0 | 0 | 1.04
11 | 32 | 1e-07 | 0.013 | 0 | 0 | 1.04
12 | 36 | 1e-07 | 0.0075 | 0 | 0 | 1.04
13 | 17 | 1e-07 | 0.0033 | 0 | 0 | 1.04
14 | 41 | 1e-07 | 0.0015 | 0 | 0 | 1
15 | 42 | 1e-07 | 0.0015 | 0 | 0 | 1
1 | 18 | 1e-07 | 0.003 | 0 | 0 | 1
17 | 36 | 0.0005 | 0.0045 | 0.32 | 0 | 1
18 | 49 | 0.0076 | 0.1141 | 1.16 | 0 | 1
18 | 50 | 0.0012 | 0.0288 | 2.06 | 0 | 1
19 | 68 | 0.0016 | 0.0195 | 0.304 | 0 | 1
20 | 19 | 0.0007 | 0.0138 | 0 | 0 | 1.06
21 | 68 | 0.0008 | 0.0135 | 0.2548 | 0 | 1
22 | 21 | 0.0008 | 0.014 | 0.2565 | 0 | 1
23 | 22 | 0.0006 | 0.0096 | 0.1846 | 0 | 1
24 | 23 | 0.0022 | 0.035 | 0.361 | 0 | 1
24 | 68 | 0.0003 | 0.0059 | 0.068 | 0 | 1
25 | 54 | 0.007 | 0.0086 | 0.146 | 0 | 1
26 | 25 | 0.0032 | 0.0323 | 0.531 | 0 | 1
27 | 37 | 0.0013 | 0.0173 | 0.3216 | 0 | 1
27 | 26 | 0.0014 | 0.0147 | 0.2396 | 0 | 1
28 | 26 | 0.0043 | 0.0474 | 0.7802 | 0 | 1
29 | 26 | 0.0057 | 0.0625 | 1.029 | 0 | 1
29 | 28 | 0.0014 | 0.0151 | 0.249 | 0 | 1
30 | 53 | 0.0008 | 0.0074 | 0.48 | 0 | 1
30 | 61 | 0.00095 | 0.00915 | 0.58 | 0 | 1
31 | 30 | 0.0013 | 0.0187 | 0.333 | 0 | 1
31 | 53 | 0.0016 | 0.0163 | 0.25 | 0 | 1
32 | 30 | 0.0024 | 0.0288 | 0.488 | 0 | 1
33 | 32 | 0.0008 | 0.0099 | 0.168 | 0 | 1
34 | 33 | 0.0011 | 0.0157 | 0.202 | 0 | 1
34 | 35 | 0.0001 | 0.0074 | 0 | 0 | 0.946
36 | 34 | 0.0033 | 0.0111 | 1.45 | 0 | 1
36 | 61 | 0.0011 | 0.0098 | 0.68 | 0 | 1
37 | 68 | 0.0007 | 0.0089 | 0.1342 | 0 | 1
38 | 31 | 0.0011 | 0.0147 | 0.247 | 0 | 1
38 | 33 | 0.0036 | 0.0444 | 0.693 | 0 | 1
40 | 41 | 0.006 | 0.084 | 3.15 | 0 | 1
40 | 48 | 0.002 | 0.022 | 1.28 | 0 | 1
41 | 42 | 0.004 | 0.06 | 2.25 | 0 | 1
42 | 18 | 0.004 | 0.06 | 2.25 | 0 | 1
43 | 17 | 0.0005 | 0.0276 | 0 | 0 | 1
44 | 39 | 1e-07 | 0.0411 | 0 | 0 | 1
44 | 43 | 0.0001 | 0.0011 | 0 | 0 | 1
45 | 35 | 0.0007 | 0.0175 | 1.39 | 0 | 1
45 | 39 | 1e-07 | 0.0839 | 0 | 0 | 1
45 | 44 | 0.0025 | 0.073 | 0 | 0 | 1
46 | 38 | 0.0022 | 0.0284 | 0.43 | 0 | 1
47 | 53 | 0.0013 | 0.0188 | 1.31 | 0 | 1
48 | 47 | 0.00125 | 0.0134 | 0.8 | 0 | 1
49 | 46 | 0.0018 | 0.0274 | 0.27 | 0 | 1
51 | 45 | 0.0004 | 0.0105 | 0.72 | 0 | 1
51 | 50 | 0.0009 | 0.0221 | 1.62 | 0 | 1
52 | 37 | 0.0007 | 0.0082 | 0.1319 | 0 | 1
52 | 55 | 0.0011 | 0.0133 | 0.2138 | 0 | 1
54 | 53 | 0.0035 | 0.0411 | 0.6987 | 0 | 1
55 | 54 | 0.0013 | 0.0151 | 0.2572 | 0 | 1
56 | 55 | 0.0013 | 0.0213 | 0.2214 | 0 | 1
57 | 56 | 0.0008 | 0.0128 | 0.1342 | 0 | 1
58 | 57 | 0.0002 | 0.0026 | 0.0434 | 0 | 1
59 | 58 | 0.0006 | 0.0092 | 0.113 | 0 | 1
60 | 57 | 0.0008 | 0.0112 | 0.1476 | 0 | 1
60 | 59 | 0.0004 | 0.0046 | 0.078 | 0 | 1
61 | 60 | 0.0023 | 0.0363 | 0.3804 | 0 | 1
63 | 58 | 0.0007 | 0.0082 | 0.1389 | 0 | 1
63 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
63 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
65 | 62 | 0.0004 | 0.0043 | 0.0729 | 0 | 1
65 | 64 | 0.0016 | 0.0435 | 0 | 0 | 1.06
66 | 56 | 0.0008 | 0.0129 | 0.1382 | 0 | 1
66 | 65 | 0.0009 | 0.0101 | 0.1723 | 0 | 1
67 | 66 | 0.0018 | 0.0217 | 0.366 | 0 | 1
68 | 67 | 0.0009 | 0.0094 | 0.171 | 0 | 1
27 | 53 | 0.032 | 0.32 | 0.41 | 0 | 1

## Advanced Setting
This sheet summaries advanced settings.
Item | Value
Discretization method | 2
Linearization times | 1
Discretization damping flag | 1
Direct feedthrough | 0
Power flow algorithm | 2
Enable (create simulink model) | 0
Enable (plot pole map) | 1
Enable (plot admittance) | 0
Enable (print output) | 1
Enable (plot swing) | 0
Enable (modal analysis) | 0